REF 	:  C12R1ED511

PERFORMANCE DATA				          ALSTOM Limited							ISSUE :  B

INDUSTRIAL PRODUCT UNIT						PAGE	:  1 OF 6

DATE	:  06.04.2000

SQUIRREL CAGE CRANE DUTY MOTOR	      SUPPLY SYSTEM  : 3 PH.,415V±10%,50HZ±3%

AMB.TEMP            : 40°C

CLASS OF INSUL. :  ‘F’

4 POLES													      Duty-S3-6 STARTS PER HOUR

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  |  | 100% CDF |  |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMPS | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT |  | KW | RPM | AMPS | ST. AMPS | ST. TORQ | POT |  | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (xFLC) | (xFLT) | (xFLT) |  |  |  | (xFLC) | (x FLT) | (xFLT) |  |  |  |  | (XFLC) | (XFLT) | (XFLT) |  |  |  |  | (XFLC) | (X FLT) | (XFLT) | (KGm²) |
| CD80 | 0.90 | 1375 | 3.48 | 3.00 | 2.00 | 2.10 | 0.80 | 1335 | 2.80 | 3.40 | 2.35 | 2.40 |  | 0.80 | 1335 | 2.80 | 3.40 | 2.35 | 2.40 |  | 0.75 | 1350 | 2.70 | 3.55 | 2.50 | 2.60 | 0.0054 |
| CD90S | 1.35 | 1290 | 3.30 | 3.80 | 2.00 | 2.00 | 1.25 | 1315 | 3.00 | 4.20 | 2.10 | 2.10 |  | 1.25 | 1315 | 3.00 | 4.20 | 2.10 | 2.10 |  | 1.10 | 1360 | 2.67 | 4.60 | 2.60 | 2.60 | 0.0100 |
| CD90L | 1.90 | 1280 | 5.30 | 2.80 | 2.00 | 2.00 | 1.70 | 1290 | 4.95 | 3.2 | 2.38 | 2.35 |  | 1.60 | 1295 | 4.75 | 3.4 | 2.55 | 2.55 |  | 1.50 | 1300 | 4.65 | 3.6 | 2.75 | 2.75 | 0.0126 |
| CD100L | 3.00 | 1340 | 7.10 | 4.10 | 1.85 | 2.10 | 2.80 | 1355 | 6.60 | 4.40 | 2.00 | 2.25 |  | 2.50 | 1380 | 5.90 | 4.90 | 2.30 | 2.60 |  | 2.20 | 1395 | 5.30 | 5.50 | 2.60 | 2.90 | 0.0279 |
| CD100L2 | 3.40 | 1345 | 7.30 | 4.50 | 2.00 | 2.25 | 3.10 | 1365 | 6.50 | 5.15 | 2.25 | 2.50 |  | 2.80 | 1385 | 5.90 | 5.60 | 2.50 | 2.80 |  | 2.60 | 1395 | 5.40 | 6.15 | 2.70 | 3.00 | 0.0360 |
| *CD112M | 4.80 | 1420 | 10.00 | 5.60 | 2.20 | 3.00 | 4.30 | 1430 | 8.90 | 6.20 | 2.50 | 3.40 |  | 3.90 | 1438 | 8.10 | 6.80 | 2.70 | 3.60 |  | 3.70 | 1440 | 7.90 | 7.00 | 2.80 | 3.70 | 0.0500 |
| *CD132S | 6.60 | 1435 | 15.1 | 5.60 | 2.30 | 3.10 | 5.90 | 1445 | 13.9 | 6.10 | 2.50 | 3.60 |  | 5.30 | 1450 | 13.0 | 6.50 | 2.80 | 4.00 |  | 5.00 | 1455 | 12.6 | 6.70 | 3.00 | 4.20 | 0.0960 |
| *CD132M | 8.70 | 1385 | 18.4 | 5.10 | 2.20 | 2.70 | 8.00 | 1395 | 17.0 | 5.60 | 2.50 | 3.00 |  | 7.50 | 1405 | 15.9 | 5.70 | 2.70 | 3.20 |  | 6.80 | 1415 | 14.4 | 6.10 | 3.00 | 3.40 | 0.1200 |
| CD160M | 15.0 | 1425 | 29.00 | 4.85 | 2.20 | 2.50 | 13.0 | 1440 | 25.3 | 5.60 | 2.60 | 2.90 |  | 12.0 | 1445 | 23.5 | 5.85 | 2.80 | 3.10 |  | 11.0 | 1450 | 21.5 | 6.50 | 2.90 | 3.40 | 0.2380 |
| CD160L | 20.0 | 1425 | 38.00 | 5.00 | 2.30 | 2.60 | 17.0 | 1440 | 32.5 | 5.80 | 2.70 | 3.00 |  | 15.5 | 1445 | 29.5 | 6.30 | 3.00 | 3.40 |  | 14.0 | 1450 | 27.0 | 6.95 | 3.30 | 3.70 | 0.2600 |
| CD180M | 24.0 | 1455 | 48.5 | 4.30 | 1.80 | 2.00 | 21.0 | 1460 | 42.5 | 4.95 | 2.00 | 2.30 |  | 18.5 | 1465 | 35.0 | 5.80 | 2.30 | 2.70 |  | 17.0 | 1467 | 33.5 | 6.10 | 2.50 | 2.90 | 0.4160 |
| CD180L | 28.0 | 1460 | 53.3 | 5.00 | 1.85 | 2.3 | 25.0 | 1465 | 48.2 | 5.4 | 2.00 | 2.50 |  | 22.0 | 1470 | 41.0 | 6.0 | 2.2 | 2.8 |  | 20.0 | 1472 | 40.5 | 6.5 | 2.7 | 3.2 | 0.698 |
| CD200L | 37.0 | 1462 | 72.0 | 4.8 | 2.00 | 2.3 | 34.0 | 1465 | 66.0 | 5.3 | 2.15 | 2.55 |  | 30.0 | 1470 | 58.5 | 6.0 | 2.5 | 2.9 |  | 27.0 | 1474 | 54.0 | 6.3 | 2.7 | 3.2 | 1.257 |

4 POLES													Duty-S4-150 STARTS PER HOUR(F.I.=1.00)

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  |  | 60% CDF |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT | KW |  | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  |  | (XFLC) | (XFLT) | (XFLT) |  |  |  | (XFLC) | (XFLT) | (XFLT) |  |  |  | (XFLC) | (X FLT) | (XFLT) | (KGm²) |
| CD80 | 0.90 | 1375 | 3.48 | 3.00 | 2.00 | 2.10 | 0.80 |  | 1335 | 2.80 | 3.40 | 2.35 | 2.40 | 0.80 | 1335 | 2.80 | 3.40 | 2.35 | 2.40 | 0.73 | 1355 | 2.64 | 3.70 | 2.6 | 2.70 | 0.0054 |
| CD90S | 1.35 | 1290 | 3.30 | 3.80 | 2.00 | 2.00 | 1.25 |  | 1315 | 3.00 | 4.20 | 2.10 | 2.10 | 1.16 | 1335 | 2.80 | 4.50 | 2.35 | 2.35 | 1.07 | 1355 | 2.60 | 4.80 | 2.55 | 2.55 | 0.0100 |
| CD90L | 1.90 | 1280 | 5.30 | 2.8 | 2.00 | 2.00 | 1.70 |  | 1290 | 4.95 | 3.2 | 2.38 | 2.35 | 1.58 | 1295 | 4.70 | 3.2 | 2.60 | 2.60 | 1.46 | 1305 | 4.50 | 3.6 | 2.8 | 2.80 | 0.0126 |
| CD100L | 2.50 | 1380 | 5.90 | 4.90 | 2.30 | 2.60 | 2.30 |  | 1390 | 5.40 | 5.50 | 2.50 | 2.85 | 2.18 | 1400 | 5.15 | 5.70 | 2.65 | 3.00 | 2.05 | 1405 | 5.00 | 5.85 | 2.85 | 3.20 | 0.0279 |
| CD100L2 | 2.91 | 1375 | 6.00 | 5.50 | 2.40 | 2.70 | 2.72 |  | 1385 | 5.60 | 6.00 | 2.60 | 2.90 | 2.57 | 1395 | 5.30 | 6.30 | 2.80 | 3.05 | 2.43 | 1400 | 5.00 | 6.60 | 2.9 | 3.20 | 0.0360 |
| CD112M | 3.89 | 1435 | 8.10 | 6.80 | 2.70 | 3.50 | 3.70 |  | 1440 | 7.90 | 7.00 | 2.80 | 3.70 | 3.54 | 1445 | 7.60 | 7.30 | 2.90 | 3.90 | 3.38 | 1450 | 6.90 | 7.90 | 3.3 | 4.40 | 0.0500 |
| CD132S | 5.02 | 1455 | 12.5 | 6.70 | 3.00 | 4.20 | 4.82 |  | 1455 | 12.2 | 6.85 | 3.10 | 4.30 | 4.65 | 1455 | 12.0 | 7.00 | 3.20 | 4.30 | 4.48 | 1460 | 11.7 | 7.20 | 3.4 | 4.50 | 0.0960 |
| CD132M | 7.10 | 1410 | 15.0 | 6.20 | 2.80 | 3.20 | 6.75 |  | 1415 | 14.5 | 6.40 | 3.00 | 3.50 | 6.47 | 1420 | 13.9 | 6.70 | 3.10 | 3.60 | 6.19 | 1425 | 13.4 | 7.00 | 3.2 | 3.80 | 0.1200 |
| CD160M | 10.70 | 1450 | 20.8 | 6.60 | 3.10 | 3.60 | 10.3 |  | 1450 | 20.0 | 6.90 | 3.10 | 3.60 | 10.05 | 1455 | 19.8 | 7.00 | 3.20 | 3.70 | 9.73 | 1455 | 19.2 | 7.30 | 3.40 | 3.80 | 0.2380 |
| CD160L | 13.15 | 1455 | 25.6 | 7.30 | 3.60 | 4.00 |  | 12.8 | 1455 | 25.0 | 7.50 | 3.70 | 4.00 | 12.52 | 1455 | 24.7 | 7.55 | 3.80 | 4.10 | 12.2 | 1457 | 24.0 | 7.85 | 3.90 | 4.20 | 0.2600 |
| CD180M | 17.80 | 1465 | 34.7 | 6.00 | 2.40 | 2.80 |  | 15.0 | 1470 | 30.5 | 6.80 | 2.90 | 3.30 | 14.65 | 1472 | 30.6 | 6.85 | 2.85 | 3.35 | 13.7 | 1474 | 29.2 | 7.15 | 3.10 | 3.60 | 0.4160 |
| CD180L | 21.2 | 1467 | 42.7 | 6.0 | 2.6 | 3.0 |  | 17.9 | 1472 | 37.0 | 7.00 | 2.8 | 3.5 | 17.44 | 1475 | 36.3 | 7.4 | 2.9 | 3.6 | 16.3 | 1477 | 35.0 | 7.7 | 3.1 | 3.9 | 0.698 |
| CD200L | 26.65 | 1475 | 53.5 | 6.4 | 2.75 | 3.30 |  | 22.5 | 1477 | 48.2 | 7.11 | 3.2 | 3.8 | 21.9 | 1478 | 46.7 | 7.4 | 3.4 | 4.0 | 20.5 | 1480 | 44.3 | 8.25 | 3.6 | 4.3 | 1.257 |

*  As per IPSS

REF 	:  C12R1ED511

PERFORMANCE DATA					   ALSTOM Limited							ISSUE :  B

INDUSTRIAL PRODUCT UNIT						PAGE	:  2 OF 6

DATE	:  06.04.2000

SQUIRREL CAGE CRANE DUTY MOTOR	      SUPPLY SYSTEM  : 3 PH.,415V±10%,50HZ±3%

AMB.TEMP            : 40°C

CLASS OF INSUL. :  ‘F’

4 POLES													Duty-S4-300 STARTS PER HOUR(F.I.=1.00)

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  | (XFLC) | (XFLT) | (XFLT) |  |  |  | (XFLC) | (X FLT) | (X FLT) |  |  |  | (XFLC) | (XFLT) | (XFLT) | (KGm²) |
| CD80 | 0.90 | 1375 | 3.48 | 3.00 | 2.00 | 2.10 | 0.80 | 1335 | 2.80 | 2.40 | 2.35 | 2.40 | 0.77 | 1347 | 2.80 | 3.50 | 2.50 | 2.50 | 0.72 | 1355 | 2.70 | 3.60 | 2.60 | 2.70 | 0.0054 |
| CD90S | 1.30 | 1305 | 3.20 | 3.95 | 2.00 | 2.00 | 1.20 | 1330 | 2.92 | 4.30 | 2.25 | 2.25 | 1.10 | 1360 | 2.67 | 4.60 | 2.60 | 2.60 | 1.04 | 1360 | 2.50 | 5.00 | 2.65 | 2.65 | 0.0100 |
| CD90L | 1.75 | 1290 | 5.05 | 3.2 | 2.30 | 2.30 | 1.60 | 1295 | 4.75 | 3.4 | 2.55 | 2.55 | 1.50 | 1300 | 3.6 | 3.6 | 2.75 | 2.75 | 1.42 | 1305 | 4.30 | 3.65 | 2.90 | 2.90 | 0.0126 |
| CD100L | 2.10 | 1405 | 5.00 | 6.00 | 2.75 | 3.10 | 2.05 | 1405 | 5.00 | 5.85 | 2.85 | 3.20 | 2.00 | 1410 | 4.80 | 6.00 | 2.90 | 3.30 | 1.93 | 1415 | 4.70 | 6.30 | 3.00 | 3.40 | 0.0279 |
| CD100L2 | 2.50 | 1400 | 5.10 | 6.50 | 2.85 | 3.10 | 2.40 | 1405 | 4.90 | 6.70 | 3.00 | 3.30 | 2.35 | 1405 | 4.80 | 6.90 | 3.00 | 3.40 | 2.30 | 1410 | 4.70 | 7.00 | 3.10 | 3.40 | 0.0360 |
| CD112M | 3.20 | 1450 | 7.00 | 8.00 | 3.30 | 4.30 | 3.20 | 1450 | 7.00 | 8.00 | 3.30 | 4.30 | 3.20 | 1450 | 7.00 | 8.00 | 3.30 | 4.30 | 3.10 | 1450 | 6.80 | 8.10 | 3.40 | 4.50 | 0.0500 |
| CD132S | 4.10 | 1460 | 11.3 | 7.40 | 3.50 | 5.00 | 4.10 | 1460 | 11.3 | 7.40 | 3.50 | 5.00 | 4.10 | 1460 | 11.3 | 7.40 | 3.50 | 5.00 | 4.10 | 1460 | 11.3 | 7.40 | 3.50 | 5.00 | 0.0960 |
| CD132M | 5.90 | 1425 | 13.0 | 7.10 | 3.40 | 4.00 | 5.80 | 1427 | 12.7 | 7.20 | 3.45 | 4.10 | 5.80 | 1427 | 12.7 | 7.20 | 3.45 | 4.10 | 5.70 | 1420 | 11.5 | 7.20 | 3.50 | 4.20 | 0.1200 |
| CD160M | 10.0 | 1455 | 19.7 | 7.00 | 3.30 | 3.70 | 9.70 | 1455 | 19.0 | 7.30 | 3.40 | 3.80 | 9.40 | 1457 | 18.5 | 7.50 | 3.60 | 4.00 | 8.80 | 1460 | 17.8 | 7.85 | 3.80 | 4.40 | 0.2380 |
| CD160L | 14.3 | 1450 | 27.5 | 6.80 | 3.30 | 3.60 | 12.1 | 1457 | 23.9 | 7.90 | 3.95 | 4.25 | 11.77 | 1460 | 23.2 | 8.15 | 4.00 | 4.60 | 11.0 | 1462 | 22.5 | 8.36 | 4.20 | 4.60 | 0.2600 |
| CD180M | 15.3 | 1470 | 31.7 | 6.60 | 2.75 | 3.30 | 13.0 | 1475 | 28.3 | 7.40 | 3.25 | 3.80 | 12.60 | 1471 | 27.5 | 7.60 | 3.30 | 3.90 | 11.8 | 1473 | 26.5 | 8.00 | 2.60 | 4.20 | 0.4160 |
| CD180L | 18.3 | 1474 | 37.8 | 7.0 | 2.8 | 3.40 | 15.5 | 1476 | 34.3 | 7.85 | 3.3 | 4.2 | 15.1 | 1479 | 33.4 | 8.0 | 3.4 | 4.2 | 14.1 | 1480 | 32.1 | 8.4 | 2.6 | 4.5 | 0.698 |
| CD200L | 22.3 | 1478 | 47.8 | 7.20 | 3.3 | 3.90 | 18.9 | 1480 | 42.4 | 8.05 | 3.9 | 4.6 | 18.4 | 1482 | 41.0 | 8.4 | 3.9 | 4.7 | 17.2 | 1482 | 39.7 | 8.6 | 2.2 | 5.0 | 1.257 |

REF 	:  C12R1ED511

PERFORMANCE DATA					   ALSTOM Limited							ISSUE :  B

INDUSTRIAL PRODUCT UNIT						PAGE	:  3 OF 6

DATE	:  06.04.2000

SQUIRREL CAGE CRANE DUTY MOTOR	      SUPPLY SYSTEM  : 3 PH.,415V±10%,50HZ±3%

AMB.TEMP            : 40°C

CLASS OF INSUL. :  ‘F’

6 POLES													       Duty-S3-6 STARTS PER HOUR

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  | (X FLC) | (X FLT) | (X FLT) |  |  |  | (XFLC) | (X FLT) | ( XFLT) |  |  |  | (XFLC) | (X FLT) | ( XFLT) | (KGm²) |
| CD80 | 0.60 | 890 | 2.40 | 3.00 | 1.70 | 2.00 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.0054 |
| CD90S | 0.80 | 860 | 2.30 | 3.50 | 2.00 | 2.10 | 0.70 | 840 | 2.00 | 4.00 | 2.30 | 2.45 | 0.70 | 840 | 2.00 | 4.00 | 2.30 | 2.45 | 0.70 | 840 | 2.00 | 4.00 | 2.30 | 2.45 | 0.0100 |
| CD90L | 1.30 | 900 | 3.80 | 3.40 | 1.60 | 2.00 | 1.10 | 915 | 3.50 | 3.80 | 1.90 | 2.30 | 1.00 | 880 | 3.30 | 4.00 | 2.40 | 2.50 | 1.00 | 925 | 3.30 | 4.00 | 2.10 | 2.60 | 0.0126 |
| CD100L | 1.60 | 885 | 3.75 | 4.30 | 2.25 | 2.30 | 1.40 | 905 | 3.30 | 5.10 | 2.70 | 2.70 | 1.30 | 890 | 3.10 | 5.50 | 2.80 | 2.90 | 1.30 | 890 | 3.10 | 5.50 | 2.80 | 2.90 | 0.0300 |
| *CD112M | 3.00 | 820 | 7.60 | 3.50 | 1.90 | 1.85 | 2.30 | 885 | 5.70 | 4.70 | 2.50 | 2.60 | 1.90 | 910 | 4.85 | 5.50 | 3.20 | 3.20 | 1.80 | 915 | 4.60 | 5.70 | 3.40 | 3.40 | 0.0360 |
| *CD132MA | 4.00 | 935 | 9.50 | 5.50 | 2.40 | 3.00 | 3.00 | 955 | 7.80 | 6.00 | 3.20 | 4.00 | 2.70 | 960 | 7.20 | 6.40 | 3.60 | 4.40 | 2.50 | 960 | 7.00 | 6.50 | 3.90 | 4.50 | 0.1050 |
| *CK132M | 7.50 | 920 | 15.0 | 5.20 | 2.10 | 2.60 | 6.40 | 935 | 13.0 | 6.00 | 2.50 | 3.00 | 5.70 | 940 | 11.8 | 6.10 | 2.70 | 3.50 | 5.40 | 945 | 11.20 | 6.40 | 2.85 | 3.70 | 0.2450 |
| *CD160M | 11.0 | 935 | 22.5 | 4.30 | 1.70 | 2.00 | 7.80 | 955 | 15.5 | 5.90 | 2.50 | 3.00 | 6.90 | 965 | 13.5 | 6.40 | 2.80 | 3.30 | 6.30 | 965 | 13.00 | 6.60 | 3.00 | 3.70 | 0.2990 |
| *CD160L | 15.0 | 940 | 31.0 | 4.30 | 1.90 | 2.30 | 12.0 | 950 | 24.5 | 5.35 | 2.50 | 2.90 | 11.0 | 955 | 22.5 | 5.70 | 2.55 | 3.00 | 10.0 | 960 | 20.50 | 6.20 | 2.90 | 3.40 | 0.2990 |
| *CD180L | 20.0 | 970 | 41.5 | 4.70 | 2.00 | 2.30 | 17.0 | 975 | 35.7 | 5.50 | 2.50 | 2.70 | 15.0 | 973 | 32.8 | 6.00 | 2.65 | 3.00 | 13.5 | 975 | 29.80 | 6.70 | 2.90 | 3.40 | 0.7060 |
| *CD200L | 25.0 | 972 | 56.8 | 5.60 | 2.60 | 2.50 | 23.8 | 975 | 49 | 6.04 | 3.36 | 2.60 | 20.8 | 978 | 50.0 | 6.00 | 3.40 | 3.00 | 19.0 | 985 | 44.00 | 6.30 | 4.2 | 3.30 | 1.1050 |

6 POLES													Duty-S4-150 STARTS PER HOUR(F.I.=1.00)

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMPS | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT |  | KW | RPM | AMPS | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | (x FLT) |  |  |  | (XFLC) | (XFLT) | (XFLT) |  |  |  |  | (X FLC) | (X FLT) | (XFLT) |  |  |  | (XFLC) | (XFLT) | (XFLT) | (KGm²) |
| CD80 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 |  | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.49 | 873 | 2.10 | 3.20 | 2.20 | 2.60 | 0.0054 |
| CD90S | 0.70 | 840 | 2.00 | 4.00 | 2.30 | 2.45 | 0.70 | 840 | 2.00 | 4.00 | 2.30 | 2.45 |  | 0.70 | 840 | 2.00 | 4.00 | 2.30 | 2.45 | 0.69 | 840 | 1.97 | 4.00 | 2.40 | 2.50 | 0.0100 |
| CD90L | 1.10 | 915 | 3.50 | 3.80 | 1.90 | 2.30 | 1.10 | 915 | 3.50 | 3.80 | 1.90 | 2.30 |  | 1.08 | 920 | 3.30 | 3.90 | 2.00 | 2.50 | 0.98 | 930 | 3.10 | 4.00 | 2.20 | 2.70 | 0.0126 |
| CD100L | 1.60 | 885 | 3.75 | 4.30 | 2.25 | 2.30 | 1.40 | 905 | 3.30 | 5.10 | 2.70 | 2.70 |  | 1.30 | 910 | 3.10 | 5.50 | 2.80 | 2.90 | 1.25 | 920 | 3.00 | 5.70 | 3.00 | 3.10 | 0.0300 |
| CD112M | 2.20 | 890 | 5.50 | 4.60 | 2.70 | 2.70 | 2.00 | 905 | 5.00 | 5.20 | 3.00 | 3.00 |  | 1.90 | 910 | 4.85 | 5.50 | 3.20 | 3.20 | 1.70 | 920 | 4.50 | 6.00 | 3.70 | 3.70 | 0.0360 |
| CD132MA | 2.70 | 960 | 7.20 | 6.40 | 3.60 | 4.40 | 2.54 | 960 | 7.20 | 6.40 | 3.80 | 4.70 |  | 2.40 | 960 | 6.90 | 6.50 | 3.90 | 5.00 | 2.50 | 960 | 7.00 | 6.50 | 3.90 | 4.50 | 0.1050 |
| CK132M | 6.20 | 940 | 12.60 | 6.00 | 2.55 | 3.20 | 5.50 | 945 | 11.50 | 6.30 | 2.70 | 3.60 |  | 5.20 | 950 | 11.20 | 6.50 | 3.00 | 3.70 | 5.00 | 950 | 11.0 | 6.90 | 3.20 | 4.00 | 0.2450 |
| CD160M | 7.10 | 960 | 14.00 | 6.20 | 2.70 | 3.30 | 6.60 | 960 | 13.50 | 6.50 | 2.90 | 3.50 |  | 5.90 | 965 | 12.20 | 7.00 | 3.20 | 4.00 | 5.50 | 965 | 11.6 | 7.20 | 3.45 | 4.20 | 0.2990 |
| CD160L | 11.40 | 955 | 23.90 | 5.50 | 2.50 | 3.00 | 10.5 | 960 | 22.50 | 5.70 | 2.75 | 3.20 |  | 9.40 | 963 | 20.30 | 6.40 | 3.10 | 3.70 | 8.80 | 965 | 18.9 | 6.80 | 3.30 | 3.90 | 0.2990 |
| CD180L | 14.50 | 975 | 32.50 | 6.00 | 2.80 | 3.10 | 13.4 | 978 | 30.00 | 6.50 | 3.00 | 3.50 |  | 11.90 | 982 | 27.00 | 7.20 | 3.40 | 3.90 | 11.20 | 980 | 26.4 | 7.30 | 3.60 | 4.10 | 0.7060 |
| CD200L | 21.00 | 978 | 50.80 | 5.90 | 3.20 | 3.00 | 19.4 | 980 | 47.30 | 6.15 | 3.50 | 3.20 |  | 17.30 | 982 | 44.00 | 6.85 | 3.85 | 3.65 | 16.20 | 983 | 44.3 | 6.70 | 4.00 | 3.90 | 1.1050 |

*  As per IPSS

REF 	:  C12R1ED511

PERFORMANCE DATA					   ALSTOM Limited							ISSUE :  B

INDUSTRIAL PRODUCT UNIT						PAGE	:  4 OF 6

DATE	:  06.04.2000

SQUIRREL CAGE CRANE DUTY MOTOR	      SUPPLY SYSTEM  : 3 PH.,415V±10%,50HZ±3%

AMB.TEMP            : 40°C

CLASS OF INSUL. :  ‘F’

6 POLES												Duty-S4-300 STARTS PER HOUR(F.I.=1.00)

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMPS | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMPS | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  | (XFLC) | (XFLT) | ( XFLT) |  |  |  | (XFLC) | (X FLT) | (XFLT) | (KGm²) |
| CD80 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.50 | 915 | 2.20 | 3.50 | 2.10 | 2.40 | 0.48 | 920 | 2.15 | 3.25 | 2.30 | 2.65 | 0.0054 |
| CD90S | 0.70 | 885 | 2.00 | 4.00 | 2.30 | 2.45 | 0.70 | 885 | 2.00 | 4.00 | 2.30 | 2.45 | 0.70 | 885 | 2.00 | 4.00 | 2.30 | 2.45 | 0.67 | 895 | 1.95 | 4.00 | 2.45 | 2.60 | 0.0100 |
| CD90L | 1.10 | 915 | 3.50 | 3.80 | 1.90 | 2.30 | 1.10 | 915 | 3.50 | 3.80 | 1.90 | 2.30 | 1.05 | 925 | 3.20 | 4.00 | 2.00 | 2.55 | 0.94 | 935 | 3.10 | 4.00 | 2.30 | 2.90 | 0.0126 |
| CD100L | 1.43 | 900 | 3.50 | 4.50 | 2.60 | 2.65 | 1.34 | 910 | 3.30 | 5.00 | 2.80 | 2.85 | 1.28 | 915 | 3.20 | 5.00 | 2.90 | 3.00 | 0.93 | 940 | 2.50 | 6.00 | 4.00 | 4.20 | 0.0300 |
| CD112M | 2.00 | 905 | 5.00 | 5.20 | 3.00 | 3.00 | 1.85 | 915 | 4.80 | 5.50 | 3.30 | 3.30 | 1.76 | 920 | 4.60 | 5.60 | 3.50 | 3.50 | 1.67 | 925 | 4.50 | 5.50 | 3.70 | 3.70 | 0.0360 |
| CD132MA | 2.30 | 965 | 7.00 | 7.00 | 3.80 | 5.30 | 2.22 | 965 | 6.90 | 7.00 | 4.00 | 5.50 | 2.18 | 965 | 6.90 | 7.00 | 4.00 | 5.50 | 2.14 | 965 | 6.80 | 7.00 | 4.00 | 5.50 | 0.1050 |
| CK132M | 5.70 | 945 | 12.00 | 6.20 | 2.70 | 3.50 | 5.00 | 950 | 11.00 | 6.90 | 3.20 | 4.00 | 4.80 | 955 | 10.40 | 6.90 | 3.20 | 4.00 | 4.60 | 965 | 10.2 | 7.00 | 3.40 | 4.20 | 0.2450 |
| CD160M | 6.50 | 965 | 13.40 | 6.40 | 2.80 | 3.50 | 6.00 | 970 | 12.50 | 6.70 | 3.10 | 3.90 | 5.30 | 970 | 11.50 | 7.20 | 3.65 | 4.50 | 5.00 | 970 | 11.2 | 7.60 | 3.90 | 4.70 | 0.2990 |
| CD160L | 10.10 | 963 | 21.60 | 6.30 | 2.80 | 3.40 | 9.40 | 965 | 20.40 | 6.40 | 3.00 | 3.60 | 8.30 | 970 | 18.00 | 7.00 | 3.50 | 4.00 | 8.00 | 970 | 18.4 | 7.00 | 3.60 | 4.20 | 0.2990 |
| CD180L | 11.80 | 978 | 28.20 | 6.90 | 3.40 | 3.90 | 10.90 | 980 | 26.80 | 7.10 | 3.70 | 4.20 | 9.70 | 982 | 24.60 | 7.70 | 4.00 | 4.80 | 9.10 | 985 | 23.8 | 7.90 | 4.20 | 5.00 | 0.7060 |
| CD200L | 16.60 | 978 | 45.40 | 6.50 | 3.90 | 3.80 | 15.40 | 980 | 42.10 | 7.00 | 4.20 | 4.10 | 13.7 | 984 | 40.50 | 6.95 | 4.70 | 4.60 | 12.8 | 985 | 38.0 | 7.40 | 4.80 | 4.70 | 1.1050 |

REF 	:  C12R1ED511

PERFORMANCE DATA					   ALSTOM Limited							ISSUE :  B

INDUSTRIAL PRODUCT UNIT						PAGE	:  5 OF 6

DATE	:  06.04.2000

SQUIRREL CAGE CRANE DUTY MOTOR	      SUPPLY SYSTEM  : 3 PH.,415V±10%,50HZ±3%

AMB.TEMP            : 40°C

CLASS OF INSUL. :  ‘F’

8 POLES														Duty-S3-6 STARTS PER HOUR

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMPS | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMPS | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  | (XFLC) | (X FLT) | (X FLT) |  |  |  | (XFLC) | (X FLT) | (X FLT) |  |  |  | (XFLC) | (X FLT) | (XFLT) | (KGm²) |
| CD90S | 0.42 | 640 | 1.40 | 2.80 | 1.85 | 1.90 | 0.37 | 660 | 1.33 | 3.20 | 2.10 | 2.20 | 0.36 | 665 | 1.30 | 3.40 | 2.20 | 2.30 | 0.34 | 674 | 1.25 | 3.50 | 2.30 | 2.40 | 0.0100 |
| CD90L | 0.55 | 640 | 2.00 | 4.60 | 1.90 | 2.00 | 0.49 | 662 | 1.95 | 4.60 | 2.30 | 2.40 | 0.47 | 665 | 1.90 | 4.60 | 2.40 | 2.50 | 0.45 | 670 | 1.85 | 4.75 | 2.50 | 2.70 | 0.0130 |
| CD100L | 0.80 | 660 | 2.35 | 3.30 | 2.21 | 2.30 | 0.73 | 670 | 2.17 | 3.60 | 2.40 | 2.50 | 0.72 | 672 | 2.20 | 3.60 | 2.50 | 2.55 | 0.68 | 680 | 2.10 | 3.65 | 2.60 | 2.70 | 0.0360 |
| CD100L2 | 1.25 | 630 | 4.45 | 2.45 | 1.90 | 1.90 | 1.08 | 656 | 3.73 | 3.00 | 2.30 | 2.30 | 1.05 | 660 | 3.60 | 3.15 | 2.40 | 2.40 | 1.00 | 665 | 3.50 | 3.30 | 2.50 | 2.50 | 0.0360 |
| CD112M | 1.60 | 625 | 5.40 | 2.70 | 2.00 | 2.00 | 1.40 | 652 | 4.55 | 3.15 | 2.45 | 2.45 | 1.36 | 655 | 4.40 | 3.50 | 2.55 | 2.55 | 1.30 | 660 | 4.20 | 3.40 | 2.70 | 2.70 | 0.0440 |
| CD132S | 2.50 | 695 | 7.50 | 4.00 | 2.10 | 2.70 | 2.30 | 700 | 7.20 | 4.20 | 2.30 | 3.00 | 2.10 | 705 | 6.80 | 4.50 | 2.60 | 3.30 | 2.00 | 705 | 6.67 | 4.60 | 2.70 | 3.40 | 0.1060 |
| CD132M | 3.40 | 695 | 9.80 | 4.40 | 2.10 | 2.80 | 3.10 | 700 | 9.25 | 4.60 | 2.40 | 3.10 | 2.90 | 703 | 8.75 | 4.80 | 2.60 | 3.20 | 2.70 | 705 | 8.50 | 4.90 | 2.80 | 3.40 | 0.1450 |
| *CD160M | 7.50 | 675 | 17.40 | 4.10 | 1.90 | 2.30 | 6.00 | 695 | 14.3 | 4.90 | 2.50 | 3.00 | 5.40 | 700 | 13.30 | 5.35 | 2.70 | 3.20 | 4.90 | 705 | 12.0 | 5.60 | 3.10 | 3.60 | 0.2990 |
| *CD160L | 10.50 | 684 | 22.00 | 4.20 | 2.10 | 2.54 | 8.90 | 695 | 19.0 | 5.00 | 2.50 | 3.00 | 8.20 | 700 | 18.00 | 5.50 | 2.70 | 3.25 | 7.50 | 705 | 16.5 | 6.00 | 3.00 | 3.50 | 0.3300 |
| *CD180L | 15.40 | 675 | 32.60 | 4.40 | 1.90 | 2.40 | 12.70 | 690 | 26.9 | 5.37 | 2.50 | 2.90 | 11.00 | 700 | 23.90 | 6.00 | 2.90 | 3.20 | 10.0 | 730 | 24.5 | 6.00 | 3.20 | 3.50 | 0.7060 |
| *CD200L | 22.50 | 720 | 52.00 | 4.60 | 2.00 | 2.20 | 17.90 | 725 | 43.6 | 5.40 | 2.55 | 3.80 | 15.00 | 730 | 39.50 | 5.90 | 3.00 | 3.20 | 13.5 | 730 | 36.9 | 6.00 | 3.30 | 3.70 | 2.2100 |

8 POLES													Duty-S4-150 STARTS PER HOUR(F.I.=1.00)

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMPS | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMPS | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT |  | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  | (XFLC) | (X FLT) | (X FLT) |  |  |  | (XFLC) | (X FLT) | (XFLT) |  |  |  | (XFLC) | (X FLT) | (XFLT) |  | (KGm²) |
| CD90S | 0.42 | 640 | 1.40 | 2.80 | 1.85 | 1.90 | 0.37 | 660 | 1.33 | 3.20 | 2.10 | 2.20 | 0.36 | 665 | 1.30 | 3.40 | 2.20 | 2.30 | 0.34 | 674 | 1.25 | 3.50 | 2.30 | 2.40 |  | 0.0100 |
| CD90L | 0.55 | 640 | 2.00 | 4.60 | 1.90 | 2.00 | 0.49 | 662 | 1.95 | 4.60 | 2.30 | 2.40 | 0.47 | 665 | 1.90 | 4.60 | 2.40 | 2.50 | 0.45 | 670 | 1.85 | 4.75 | 2.50 | 2.70 |  | 0.0130 |
| CD100L | 0.80 | 660 | 2.35 | 3.30 | 2.21 | 2.30 | 0.73 | 670 | 2.17 | 3.60 | 2.40 | 2.50 | 0.72 | 672 | 2.20 | 3.60 | 2.50 | 2.55 | 0.66 | 682 | 2.05 | 3.85 | 2.70 | 2.80 |  | 0.0360 |
| CD100L2 | 1.25 | 630 | 4.45 | 2.45 | 1.90 | 1.90 | 1.07 | 656 | 3.65 | 3.00 | 2.30 | 2.30 | 1.04 | 660 | 3.48 | 3.15 | 2.40 | 2.40 | 0.98 | 668 | 3.33 | 3.30 | 2.60 | 2.60 |  | 0.0360 |
| CD112M | 1.60 | 625 | 5.40 | 2.70 | 2.00 | 2.00 | 1.40 | 652 | 4.55 | 3.15 | 2.45 | 2.45 | 1.36 | 655 | 4.40 | 3.50 | 2.55 | 2.55 | 1.30 | 660 | 4.20 | 3.40 | 2.70 | 2.70 |  | 0.0440 |
| CD132S | 2.20 | 700 | 6.75 | 4.60 | 2.40 | 3.00 | 2.10 | 705 | 6.80 | 4.50 | 2.60 | 3.30 | 1.97 | 708 | 6.40 | 4.80 | 2.70 | 3.50 | 1.90 | 710 | 6.30 | 4.80 | 2.70 | 3.60 |  | 0.1060 |
| CD132M | 3.00 | 700 | 9.10 | 4.80 | 2.50 | 3.10 | 2.80 | 703 | 8.60 | 5.00 | 2.60 | 3.50 | 2.70 | 705 | 8.50 | 4.90 | 2.80 | 3.40 | 2.50 | 710 | 8.00 | 5.40 | 2.90 | 3.80 |  | 0.1450 |
| CD160M | 6.00 | 695 | 14.30 | 4.90 | 2.50 | 3.00 | 5.20 | 700 | 12.90 | 4.60 | 2.70 | 3.30 | 5.00 | 702 | 12.40 | 5.80 | 2.80 | 3.40 | 4.80 | 705 | 12.20 | 5.80 | 2.90 | 3.60 |  | 0.2990 |
| CD160L | 9.10 | 695 | 19.50 | 5.00 | 2.45 | 2.95 | 7.10 | 709 | 16.00 | 6.40 | 3.20 | 3.75 | 7.70 | 705 | 17.00 | 5.90 | 2.90 | 3.45 | 7.30 | 708 | 16.50 | 6.10 | 3.05 | 3.65 |  | 0.3300 |
| CD180L | 11.50 | 695 | 24.70 | 5.90 | 2.70 | 3.00 | 9.90 | 700 | 21.80 | 6.60 | 3.00 | 3.70 | 9.70 | 705 | 21.40 | 6.60 | 3.10 | 3.80 | 9.20 | 707 | 20.80 | 6.80 | 3.40 | 4.00 |  | 0.7060 |
| CD200L | 15.50 | 725 | 40.00 | 5.80 | 2.90 | 3.20 | 13.4 | 730 | 36.70 | 6.30 | 3.35 | 3.65 | 13.0 | 730 | 35.70 | 6.40 | 3.40 | 3.70 | 12.4 | 732 | 35.00 | 6.50 | 3.60 | 3.90 |  | 2.2100 |

*  As per IPSS

REF 	:  C12R1ED511

PERFORMANCE DATA					   ALSTOM Limited							ISSUE :  B

INDUSTRIAL PRODUCT UNIT						PAGE	:  6 OF 6

DATE	:  06.04.2000

SQUIRREL CAGE CRANE DUTY MOTOR	      SUPPLY SYSTEM  : 3 PH.,415V±10%,50HZ±3%

AMB.TEMP            : 40°C

CLASS OF INSUL. :  ‘F’

8 POLES													Duty-S4-300 STARTS PER HOUR(F.I.=1.00)

| FRAME | 25% CDF |  |  |  |  |  | 40% CDF |  |  |  |  |  | 60% CDF |  |  |  |  |  | 100% CDF |  |  |  |  |  | ROTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | KW | RPM | AMPS | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMP | ST. TORQ | POT | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT | KW | RPM | AMP | ST. AMPS | ST. TORQ | POT | GD² |
| SIZE |  |  |  | (XFLC) | (X FLT) | ( XFLT) |  |  |  | (XFLC) | (X FLT) | (X FLT) |  |  |  | (XFLC) | (X FLT) | (X FLT) |  |  |  | (XFLC) | (X FLT) | ( XFLT) | (KGm²) |
| CD90S | 0.42 | 640 | 1.40 | 2.80 | 1.85 | 1.90 | 0.37 | 660 | 1.33 | 3.20 | 2.10 | 2.20 | 0.36 | 665 | 1.30 | 3.40 | 2.20 | 2.30 | 0.33 | 675 | 1.21 | 3.60 | 2.35 | 2.45 | 0.0100 |
| CD90L | 0.55 | 640 | 2.00 | 4.60 | 1.90 | 2.00 | 0.49 | 662 | 1.95 | 4.60 | 2.30 | 2.40 | 0.47 | 665 | 1.90 | 4.60 | 2.40 | 2.50 | 0.44 | 672 | 1.80 | 4.75 | 2.60 | 2.75 | 0.0130 |
| CD100L | 0.80 | 660 | 2.35 | 3.30 | 2.21 | 2.30 | 0.73 | 670 | 2.17 | 3.60 | 2.40 | 2.50 | 0.69 | 678 | 2.08 | 3.70 | 2.60 | 2.70 | 0.64 | 684 | 2.00 | 3.90 | 2.80 | 2.90 | 0.0360 |
| CD100L2 | 1.25 | 630 | 4.45 | 2.45 | 1.90 | 1.90 | 1.07 | 656 | 3.65 | 3.00 | 2.30 | 2.30 | 1.04 | 660 | 3.48 | 3.15 | 2.40 | 2.40 | 0.98 | 668 | 3.33 | 3.30 | 2.60 | 2.60 | 0.0360 |
| CD112M | 1.50 | 640 | 4.70 | 3.00 | 2.20 | 2.20 | 1.40 | 652 | 4.55 | 3.15 | 2.45 | 2.45 | 1.30 | 660 | 4.20 | 3.40 | 2.70 | 2.70 | 1.20 | 670 | 3.90 | 3.60 | 2.90 | 2.90 | 0.0440 |
| CD132S | 1.90 | 710 | 6.30 | 4.80 | 2.70 | 3.60 | 1.80 | 710 | 6.30 | 4.80 | 2.80 | 3.80 | 1.80 | 710 | 6.30 | 4.80 | 2.80 | 3.80 | 1.75 | 710 | 6.10 | 4.95 | 2.90 | 4.00 | 0.1060 |
| CD132M | 2.60 | 710 | 8.25 | 5.30 | 2.80 | 3.80 | 2.50 | 710 | 8.00 | 5.40 | 2.90 | 3.80 | 2.50 | 710 | 8.00 | 5.40 | 2.90 | 3.80 | 2.40 | 710 | 7.90 | 5.50 | 2.90 | 3.90 | 0.1450 |
| CD160M | 5.50 | 697 | 13.60 | 5.30 | 2.40 | 3.00 | 4.80 | 705 | 12.20 | 5.80 | 2.90 | 3.60 | 4.60 | 708 | 11.7 | 5.80 | 3.00 | 3.70 | 4.40 | 710 | 11.50 | 6.00 | 3.10 | 3.90 | 0.2990 |
| CD160L | 8.50 | 695 | 18.50 | 5.30 | 2.62 | 3.10 | 7.30 | 708 | 16.50 | 6.10 | 3.05 | 3.65 | 7.10 | 709 | 16.0 | 6.40 | 3.20 | 3.75 | 6.80 | 710 | 15.50 | 6.50 | 3.30 | 3.90 | 0.3300 |
| CD180L | 10.5 | 700 | 22.20 | 6.50 | 2.80 | 3.20 | 9.10 | 706 | 20.60 | 6.90 | 3.30 | 4.00 | 8.80 | 707 | 19.6 | 7.10 | 3.40 | 4.20 | 8.40 | 710 | 19.00 | 7.20 | 3.60 | 4.20 | 0.7060 |
| CD200L | 14.1 | 727 | 37.50 | 6.20 | 3.20 | 3.50 | 12.2 | 730 | 35.00 | 6.60 | 3.65 | 3.90 | 11.9 | 732 | 34.6 | 6.70 | 3.80 | 4.00 | 11.30 | 735 | 34.40 | 6.80 | 3.90 | 4.20 | 2.2100 |

| SIGN. NAME DATE | K.G.CHOUDHURY 05.04.2000 | R.RANJAN 05.04.2000 | P.MAZUMDER 06.04.2000 |
| --- | --- | --- | --- |
|  | PREPARED BY | CHECKED BY | APPROVED BY |

AMENDMENTS :

ISSUE : A, DT.14.06.97, ORIGINAL ISSUE

ISSUE : B, DT.06.04.2000, Frame size designation changed to CD/CK wherever applicable, GD² value for 160/180/200 frames revised.

FILENAME : PREPC5-C:\EDDOC\ED511.DOC